Specification for 28HE Series High Efficiency Water Boiler

Job:

Engineer:

Contractor:

Unit Tagging:

1.01. SECTION INCLUDES

A.	Boiler

B.	Safety Controls

C.	Electrical Supply

D.	Fuel Burning Equipment

1.02. REFERENCES

A.	American Society of Mechanical Engineers (ASME) Section IV - Boiler and Pressure Vessel Code.

B.	Hydronics Institute (HI) - Testing and Rating Standard for Cast Iron and Steel Heating Boilers.

C.	UL Approved Burner

1.03. SUBMITTALS

A.	Submit product data, wiring diagrams and near boiler piping schematics for manufactured heating units.

1.04. OPERATION AND MAINTENANCE DATA

A.	Submit operations and maintenance data, including manufacturer's descriptive literature, installation instructions, operating instructions and maintenance and repair data.

1.05 WARRANTY

A.	Units that do not carry a standard published warranty of ten or more years are not  acceptable to this project.  Job specific warranties are not acceptable unless executed by an authorized officer of the manufacturer under seal and submitted five (5) working days prior to the bid date of this project.

2.01 General Description

A.	Furnish and install as herein specified, (     ) new  boiler/burner  unit(s) for low pressure Water heating service and arranged for completely automatic operation firing (oil) (gas) (gas/oil). Boiler shipped Knocked-Down for field assembly by installing contractor.

B.	Each boiler shall be furnished complete with an insulated metal jacket; Forced draft burner; Cast iron smoke hood with integral 14 gauge aluminized steel damper; Pressure-tight front and rear flame observation ports with covers; Steel angle floor rails; Cast iron burner mounting plate with insulation and additional controls and devices as hereafter specified.

C.	Safety controls and limit devices shall be installed in accordance with the requirements of (NFPA 31), (BOCA), (NFPA 54). In every case, the boiler installation shall be accomplished in accordance with the recommended good practice and installation requirements of the A.S.M.E. Boiler and Pressure Vessel Code. (Section 4)

D.	The  boiler/burner  units shall have been rated in accordance with the Hydronics Institute Testing and Rating Standard for Heating Boilers, and shall be performance tested and listed by I=B=R at +0.10 inches (w.c.) draft as follows:

- Develop an I=B=R Gross Output of not less than            MBTU/Hr. when fired at a rate of          MBH natural gas or            GPH of #2 light oil.

- The unit shall provide a minimum of            % combustion efficiency and Thermal Efficiency of            % when burning Natural Gas and         % combustion efficiency and Thermal Efficiency of           % when burning Oil.

- The boiler shall have a minimum water volume of 0.9 # per MBH of Gross Output, providing thermal mass to reduce burner short cycling.

- The boiler shall have a maximum Heat Release of              BTU per Cubic Foot of Furnace volume.

E.	The  boiler/burner  units shall be Model (LO) (G) (GO)28HE-W-           as manufactured by Smith Cast Iron Boilers.

2.02	BOILER CONSTRUCTION / INSTALLATION:

A.	Boiler sections shall be manufactured from a flake graphite eutectic cell cast iron. The sections shall be of the wet base type designed for pressure firing and it shall be constructed and tested for 80 P.S.I water working pressure. In accordance with the A.S.M.E. Section IV Rules for the Construction of Heating Boilers. Individual sections will have been subjected to a hydrostatic pressure test of 200 PSIG at the factory before shipment and they shall be marked, stamped or cast with the A.S.M.E. Code symbol. Boilers with less than 200-PSIG pressure test will not be acceptable for this project. Boiler sections shall be cast in the U.S.A. to meet U.S. Steel content requirements.

B.	Boiler sections shall be of one piece design incorporating the furnace space and flue gas collector space with perimeter joints between the sections arranged for permanent pressure sealing with high temperature ceramic fiber rope. Precision CNC machined, upper and lower ports for connecting the water space of adjacent sections shall be sealed by means of a  graphite composition port connector. The port connectors will be inert and have a temperature rating of 1800 F. The port connector will meet ASTM F-37 and ASTM F-36 standards for sealability and recovery. Sections shall be assembled with short draw rods, tightened to final torque after the section assembly is complete.  The boiler shall have an oval upper supply port  to provide reduced water velocity and aid in air separation and removal.

C.	All boiler discharges shall be piped to floor drains as shown on the contract drawings and as indicated by the consulting engineer. Blowdown valves shall be brass, ball type and not less than one-inch IPS and they shall discharge to a floor drain or away from the boiler as directed by the Consulting Engineer. Pipe ends shall be cut at a 45-degree angle to prevent a cap or plug from being installed. Hangars or standoffs to prevent the valve body from undue stress or strain shall support all such discharge piping.

D.	Boiler drain valves shall be connected to the lowest water space available and shall be installed with pipe and fittings to connect the bottom blow off full size to drain.

E.	All individual sections shall have legs to provide support on both sides. Two  3" X 3"  base angles shall be furnished to be set under field assembled boilers to provide level support for the sections when shimmed and grouted to a concrete floor. The base angles shall be tapped to receive the supporting frame for the insulated metal jacket.

F.	Insulating metal jacket shall consist of 20-gauge steel panels fitted with 3” 1 1/2 Lb./Cu. Ft. density fiberglass insulation glued to the inside of the panels. Jacket panels shall be finished with blue hammertone paint baked on and shall be arranged with slots and knockouts to accommodate the boiler piping and to allow jacket installation after the piping is in place.  Left and Right side panels shall be furnished with two recessed handles located above and below the horizontal centerline of the jacket for easy removal and to provide access to the boiler clean out covers and draw rods.

G.	Clean-out covers shall be sized and located to allow full access to the extended pin type heating surface areas for cleaning and inspection of the Heat Transfer Rods.  Clean-out covers shall have grooves to contain high temperature ceramic fiber rope seals for gas-tight fit to the sections and incorporate cast iron horizontal baffles to reduce short circuiting of flue gases and also enhance performance by maximizing heat transfer.

H.	Stop valves of the outside stem and yoke type shall be provided in the supply and return pipe connections to the boiler.  Provisions shall be made for the expansion and contraction of the heating mains connected to the boiler by providing substantial anchorage at suitable points and assisted by the use of swing joints to allow the piping to expand and contract without imposing excessive forces on the boiler castings.

I.	Boiler shipped Knocked-Down for field assembly by installing contractor.

J.	Boiler installation shall be accomplished within acceptable A.S.M.E. piping practices and requirements and in strict accordance with the boiler manufacturer's recommendations and instructions.

K.	A hydrostatic pressure test of one-and-one-half times the working pressure of the boiler shall be conducted. Such tests shall be of such duration as necessary and as directed by the engineer to ensure the boiler has been assembled and installed correctly with no leaks or improper operating conditions.

L.	The installing contractor shall contact and notify the Boiler Inspections Divisions of the State when the installation of the boiler, burner and controls is substantially complete. Installing contractor shall request an Inspection of the boiler to be conducted by the State Boiler Inspector and to have a Certificate of Inspection issued upon satisfactory inspection.

2.03 	WATER TRIM:

A.	Each boiler shall be supplied with a minimum of the following trim:

1.	A.S.M.E. Schedule Side Outlet Relief Valve set for 40 PSIG.

2.	Pressure Temperature Gauge

3.	Honeywell L4006E Manual Reset High limit

4.	Honeywell L4007A Operating Temperature Control

5.	T991A Modulating Control (Select for Modulation)

5.	L4007A Low-High-Low Control (Select for Low-High-Low)

2.04	COMBUSTION SYSTEM (OIL)

A.	Each unit(s) shall include a forced draft flame retention type burner having primary air adjustment and shall be a high pressure atomizing oil burner tested by Underwriters Laboratories and complying with the rules and regulations U.L.. as well as the local authorities having jurisdiction. The burner shall be capable of firing a Series LO28HE-W-         boiler with #2 oil at the rate of             GPH of light against a furnace pressure of            inches of water column.  The Burner shall be (Beckett) (Carlin) (Power Flame) Model Number          .

B.	The burner shall be driven by a         HP 3450 RPM, 208 / 240 / 460 volts, 60 hertz,  (single) (three) phase, 60 cycle alternating current motor. Control circuit voltage shall be supplied from a separate 115 volt branch circuit.

C.	The burner shall be arranged for (Low-High-Off) (Low-High-Low) (Modulation) firing. The burner shall provide for an open damper prepurge through a damper motor.

D.	The burner shall include the appropriate oil piping and pumping to supply the nozzle arrangement, dual automatic safety shutoff valves, return oil pressure control, and combustion air damper control.

E.	Oil pressure shall be obtained from a 300 PSI fuel unit driven by the burner motor.  The fuel unit shall have two-stage pumping gears, self-contained pressure regulating valve and shall be suitable for 3450 RPM service with suction vacuum up to 15".

F.	Burner shall be equipped with an electronic flame safeguard system and scanner. The control shall be a Honeywell                    UV Flame System microprocessor-based, burner management control system with self-diagnostics and non-volatile memory.

G.	Control Panel: The burner mounted control panel shall include the following:

Indicator lights: Power-On, Main Fuel  (Low fire hold switch) (Manual potentiometer and Switch) shall be included to allow the burner to adjusted to intermediate firing positions as job conditions require.

H.	A 12,000 Volt Direct Spark Ignition Transformer for oil ignition.

2.04	COMBUSTION SYSTEM (GAS)

A.	The units shall include a forced-draft flame-retention type burner. Tested by Underwriters Laboratories and complying with the rules and regulations of U.L.  as well as the local authorities having jurisdiction. The burners shall be capable of firing a Series G28HE-W-        boiler with           MBH of natural gas against a furnace pressure of              inches of water column, with supply gas pressure of 14 inches w.c. at the inlet to the main manual shutoff cock. The Burner shall be  Power Flame Model                     .

B.	The gas train shall be U.L.  listed and shall consist of the following items:

(1)	Main Motorized Gas Valve

(2)	Auxiliary Solenoid Gas Valve

(3)	Main Gas Pressure Regulator

(4)	Maxitrol Pilot Gas Pressure Regulator

C.	The burner shall be driven by a            HP 3450 RPM, 208 / 240 / 460 volts, 60 hertz,  (single) (three) phase, 60 cycle alternating current motor. Control circuit voltage shall be supplied from a  separate 115 volt branch circuit.

D.	The burner shall be arranged for (Lo-Hi-Off) (Lo-Hi-Lo) (Modulating) firing.

E.	Burner shall be equipped with an electronic flame safeguard system and scanner. The control shall be a Honeywell                     UV Flame System microprocessor-based, burner management control system with self-diagnostics and non-volatile memory.

F.	Control Panel: The burner mounted control panel shall include the following:

Indicator lights: Power-On, Main Fuel

2.04	COMBUSTION SYSTEM (GAS-OIL)

Each unit(s) shall include a forced draft flame retention type burner having a ring of recessed gas ports with an orifice for each port, primary air adjustment and externally mounted gas pilot and a high pressure atomizing oil burner tested by Underwriters Laboratories and complying with the rules and regulations U.L., . as well as the local authorities having jurisdiction. The burner shall be capable of firing a Series GO28HE-W-        boiler with #2 oil at the rate of       GPH of light oil and        MBH of natural gas against a furnace pressure of         inches of water column, with supply gas pressure of 14 inches (w.c.) at the inlet to the main manual shutoff cock.  The Burner shall be Power Flame Model Number                  .

- The gas train shall be U.L. listed and shall consist of the following items:

  - Main Motorized Gas Valves

  - High and Low Gas Pressure Switches

  - Auxiliary Solenoid Gas Valve

  - Lubricated Shutoff Cock

  - Maxitrol Gas Pressure Regulator

- The burner shall be driven by a          HP 3450 RPM, 208 / 240 / 460 volts, 60 hertz, (single)  (three) phase alternating current motor.  Control circuit voltage shall be supplied from a  115-volt control circuit transformer.

- The burner shall be arranged for (Lo-Hi-Off) (Lo-Hi-Lo) (Modulation) firing of both fuels. The burner shall provide for an open damper prepurge through a damper motor

- The burner shall include the appropriate oil piping and pumping to supply the nozzle arrangement, dual automatic safety shutoff valves, return oil pressure control, air flow switch and combustion air damper control.

- Oil pressure shall be obtained from a 300-P.S.I.G. fuel unit driven by the burner motor.  The fuel unit shall have two-stage pumping gears, self-contained pressure regulating valve and shall be suitable for 3450 RPM service with suction vacuum up to 15" Hg.

- Burner shall be equipped with an electronic flame safeguard system and scanner. The control shall be a Honeywell UV Flame System microprocessor-based, burner management control system with self-diagnostics and non-volatile memory.

- Control Panel:

The burner mounted control panel shall include the following:

Indicator lights: Power-On, Main Fuel , (optional- Select) [ Call for Heat , Ignition , Main Flame Failure (Alarm) , Pilot Flame Failure (Alarm) , High Gas Pressure (Alarm) , Low Gas Pressure (Alarm) , Low Water (Alarm) . Alarm Bell to sound on Main Flame Failure, Pilot Flame Failure, High Gas Pressure, Low Gas Pressure, and Low Water. Alarm Reset System shall be provided to silence the Bell but the light will remain lit until the fault has been corrected ]. A (low fire hold switch) (manual pot and switch) shall be included to allow the burner to be adjusted to intermediate firing positions as job conditions require.

2.05	BURNER LIGHTOFF AND WARRANTY SERVICE

A.	The contractor shall provide factory certified lightoff for the burners and one year of warranty service on burner controls starting on the lightoff date. The warranty service shall include labor materials to replace any parts or controls, which fail in service as the result of a defect in material or manufacture.

B.	The owner shall be responsible for the cost of normal maintenance, such as replacement of filter medium, cleaning, oiling, service control system malfunction, etc., shall be paid for by the owners.

C.	The owner's operating personnel shall be instructed in the operation and maintenance of the burner and controls at the time of lightoff. The owner shall arrange to have the people who require training to be present at the lightoff.